## sheetName
| OBIS name | i100-XML.XML |  |  |  | Нартис-100 LY.XML |  |  |  | Coincidence (yes/no) |  | Total
OBIS-code |  | Description | Value Type (code) | Value Type (description) | Scaler | Description | Value Type (code) | Value Type (description) | Scaler | Set yes/no by Scaler | Set yes/no by Value Type | Success/Fail
0.0.0.1.0.255 | - | Ch. 0 Billing period counter (1) #255 | 0 | Missing data | - | Not found | - | - | - | - | - | Fail
0.0.42.0.0.255 | Логическое имя устройства | Ch. 0 COSEM Logical device name | 9 | Byte sequence | - | Ch. 0 COSEM Logical device name | 9 | Byte sequence | - | Yes | Yes | Success
0.0.43.1.2.255 | Счётчик пакетов | Ch. 0 Invocation counter #2 | 6 | 32-bit unsigned integer | - | Ch. 0 Invocation counter #2 | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.1.0.255 | Заводской номер ПУ | Ch. 0 Device ID 1, manufacturing number | 9 | Byte sequence | - | Ch. 0 Device ID 1, manufacturing number | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.1.255 | Тип ПУ | Ch. 0 Device ID #2 | 9 | Byte sequence | - | Ch. 0 Device ID #2 | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.2.255 | Версия метрологического ПО | Ch. 0 Device ID #3 | 9 | Byte sequence | - | Ch. 0 Device ID #3 | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.3.255 | Наименование производителя | Ch. 0 Device ID #4 | 9 | Byte sequence | - | Ch. 0 Device ID #4 | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.4.255 | Дата выпуска ПУ | Ch. 0 Device ID #5 | 9 | Byte sequence | - | Ch. 0 Device ID #5 | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.5.255 | - | Ch. 0 Device ID #6 | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.0.96.1.6.255 | Версия спецификации СПОДЭС | Ch. 0 Device ID #7 | 9 | Byte sequence | - | Ch. 0 Device ID #7 | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.7.255 | Схема подключения ПУ (трех или четырех проводная): 0 – трех проводная / 1 – четырех проводная | Ch. 0 Device ID #8 | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
0.0.96.1.8.255 | Идентификатор части ВПО, не относящейся к метрологии* | Ch. 0 Device ID #9 | 9 | Byte sequence | - | Ch. 0 Device ID #9 | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.9.255 | Идентификатор исполнения счетчика (модель) | Ch. 0 Device ID #10 | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.0.96.1.10.255 | Данные точки учета | Ch. 0 Metering point ID | 9 | Byte sequence | - | Ch. 0 Metering point ID | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.128.255 | Контрольная сумма не метрологической части ВПО* | Manufacturer specific | 9 | Byte sequence | - | Manufacturer specific | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.1.130.255 | - | Manufacturer specific | 9 | Byte sequence | - | Manufacturer specific | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.2.0.255 | Счетчик коррекций (конфигурирований) | Ch. 0 No. of configuration program changes | 6 | 32-bit unsigned integer | - | Ch. 0 No. of configuration program changes | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.2.1.255 | Дата последнего конфигурирования | Ch. 0 Date of last configuration program change | 9 | Byte sequence | - | Ch. 0 Date of last configuration program change | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.2.5.255 | Дата последней калибровки | Ch. 0 Date of last calibration | 9 | Byte sequence | - | Ch. 0 Date of last calibration | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.2.7.255 | Дата последнего активирования календаря | Ch. 0 Date of activation of the passive calendar | 9 | Byte sequence | - | Ch. 0 Date of activation of the passive calendar | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.2.12.255 | Дата последней установки времени | Ch. 0 Date (corrected) of last clock synchronisation / setting | 9 | Byte sequence | - | Ch. 0 Date (corrected) of last clock synchronisation / setting | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.2.13.255 | Дата последнего изменения встроенного ПО | Ch. 0 Date of last firmware activation | 9 | Byte sequence | - | Ch. 0 Date of last firmware activation | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.4.2.255 | Режим телеметрии 1 | Ch. 0 State of the internal control signals (status word #2) | 22 | Enumeration | - | Ch. 0 State of the internal control signals (status word #2) | 17 | 8-bit unsigned integer | - | Yes | No | Fail
0.0.96.4.3.255 | Блокировка реле нагрузки | Ch. 0 State of the internal control signals (status word #3) | 17 | 8-bit unsigned integer | - | Ch. 0 State of the internal control signals (status word #3) | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.96.5.2.255 | Слово состояний контроля мощности | Ch. 0 Internal operating status (status word #2) | 18 | 16-bit unsigned integer | - | Ch. 0 Internal operating status (status word #2) | 0 | Missing data | - | Yes | No | Fail
0.0.96.5.3.255 | - | Ch. 0 Internal operating status (status word #3) | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.5.4.255 | Статус качества сети | Ch. 0 Internal operating status (status word #4) | 18 | 16-bit unsigned integer | - | Ch. 0 Internal operating status (status word #4) | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.5.131.255 | Номер аварийного тарифа | Manufacturer specific | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.7.9.255 | - | Ch. 0 No. of long power failures in any phase | 18 | 16-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.7.21.255 | - | Ch. 0 No. of power failures in any phase | 18 | 16-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.8.10.255 | Длительность провала/ перенапряжения | Ch. 0 Time of operation Rate 10 | 6 | 32-bit unsigned integer | - | Ch. 0 Time of operation Rate 10 | 6 | 32-bit unsigned integer | 1 | No | Yes | Fail
0.0.96.10.1.255 | - | Ch. 0 Status register #1 | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.10.2.255 | - | Ch. 0 Status register #2 | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.10.4.255 | - | Ch. 0 Status register #4 | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.10.5.255 | - | Ch. 0 Status register #5 | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.11.0.255 | Код события | Ch. 0 Event code #1 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #1 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.11.1.255 | Код события | Ch. 0 Event code #2 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #2 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.11.2.255 | Код события | Ch. 0 Event code #3 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #3 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.11.3.255 | Код события | Ch. 0 Event code #4 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #4 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.11.4.255 | Код события | Ch. 0 Event code #5 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #5 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.11.5.255 | Код события | Ch. 0 Event code #6 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #6 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.11.6.255 | Код события | Ch. 0 Event code #7 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #7 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.11.7.255 | Код события | Ch. 0 Event code #8 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #8 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.11.8.255 | Код события | Ch. 0 Event code #9 | 18 | 16-bit unsigned integer | - | Ch. 0 Event code #9 | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
0.0.96.12.4.255 | Номер канала (интерфейс) | Ch. 0 Comm. port parameters Parameter 1 | 17 | 8-bit unsigned integer | - | Ch. 0 Comm. port parameters Parameter 1 | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.96.12.6.255 | Адрес (клиента) | Ch. 0 Comm. port parameters Telephone number / Communication address of the physical device | 9 | Byte sequence | - | Ch. 0 Comm. port parameters Telephone number / Communication address of the physical device | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.14.0.255 | текущий тариф | Ch. 0 Currently active tariff #1 | 9 | Byte sequence | - | Ch. 0 Currently active tariff #1 | 17 | 8-bit unsigned integer | - | Yes | No | Fail
0.0.96.15.0.255 | Счетчик срабатываний реле на размыкание | Ch. 0 Event counter #1 | 6 | 32-bit unsigned integer | - | Ch. 0 Event counter #1 | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.0.255 | Счетчик вскрытий корпуса | Ch. 0 Meter open event counter | 6 | 32-bit unsigned integer | - | Ch. 0 Meter open event counter | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.1.255 | Дата последнего вскрытия корпуса | Ch. 0 Meter open event, time stamp of current event occurrence | 9 | Byte sequence | - | Ch. 0 Meter open event, time stamp of current event occurrence | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.20.2.255 | Продолжительность последнего вскрытия корпуса | Ch. 0 Meter open event, duration of current event | 6 | 32-bit unsigned integer | - | Ch. 0 Meter open event, duration of current event | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.3.255 | Общая продолжительность вскрытия корпуса | Ch. 0 Meter open event, cumulative duration | 6 | 32-bit unsigned integer | - | Ch. 0 Meter open event, cumulative duration | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.5.255 | Счетчик вскрытий крышки клеммников | Ch. 0 Terminal cover open event counter | 6 | 32-bit unsigned integer | - | Ch. 0 Terminal cover open event counter | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.6.255 | Дата последнего вскрытия крышки клеммников | Ch. 0 Terminal cover open event, time stamp of current event occurrence | 9 | Byte sequence | - | Ch. 0 Terminal cover open event, time stamp of current event occurrence | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.20.7.255 | Продолжительность последнего вскрытия крышки клеммников | Ch. 0 Terminal cover open event, duration of current event | 6 | 32-bit unsigned integer | - | Ch. 0 Terminal cover open event, duration of current event | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.8.255 | Общая продолжительность вскрытия крышки клеммников | Ch. 0 Terminal cover open event, cumulative duration | 6 | 32-bit unsigned integer | - | Ch. 0 Terminal cover open event, cumulative duration | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.15.255 | Счетчик срабатываний датчика магнитного поля | Ch. 0 Strong DC magnetic field event counter | 6 | 32-bit unsigned integer | - | Ch. 0 Strong DC magnetic field event counter | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.16.255 | Дата последнего воздействия датчика магнитного поля | Ch. 0 Strong DC magnetic field event, time stamp of current event occurrence | 9 | Byte sequence | - | Ch. 0 Strong DC magnetic field event, time stamp of current event occurrence | 9 | Byte sequence | - | Yes | Yes | Success
0.0.96.20.17.255 | Продолжительность последнего воздействия магнитного поля | Ch. 0 Strong DC magnetic field event, duration of current event | 6 | 32-bit unsigned integer | - | Ch. 0 Strong DC magnetic field event, duration of current event | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.18.255 | Общая продолжительность воздействия магнитного поля | Ch. 0 Strong DC magnetic field event, cumulative duration | 6 | 32-bit unsigned integer | - | Ch. 0 Strong DC magnetic field event, cumulative duration | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.96.20.20.255 | - | Ch. 0 Supply control switch / valve tamper event counter | 2 | Structure from data of different types | - | Not found | - | - | - | - | - | Fail
0.0.96.20.21.255 | - | Ch. 0 Supply control switch / valve tamper event, time stamp of current event occurrence | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.50.0.255 | - | Ch. 0 Man. spec. abstract object | 6 | 32-bit unsigned integer | - | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Yes | No | Fail
0.0.96.50.1.255 | - | Ch. 0 Man. spec. abstract object | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.0.96.50.6.255 | - | Ch. 0 Man. spec. abstract object | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.0.96.50.11.255 | - | Ch. 0 Man. spec. abstract object | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.0.96.50.15.255 | - | Ch. 0 Man. spec. abstract object | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.50.16.255 | - | Ch. 0 Man. spec. abstract object | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.0.96.51.0.255 | Текущее состояние датчика вскрытия корпуса | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.96.51.1.255 | Текущее состояние датчика вскрытия крышки клеммников | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.96.51.3.255 | Текущее состояние датчика магнитного поля | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.96.51.5.255 | Зафиксированное состояние событий электронных пломб | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.96.51.6.255 | Обжатие электронных пломб | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.96.51.7.255 | Очистка зафиксированных событий (магнит и ВЧ поле) | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Ch. 0 Man. spec. abstract object | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.96.128.3.255 | - | Manufacturer specific | 21 | 64-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.128.4.255 | - | Manufacturer specific | 2 | Structure from data of different types | - | Not found | - | - | - | - | - | Fail
0.0.96.128.5.255 | - | Manufacturer specific | 2 | Structure from data of different types | - | Not found | - | - | - | - | - | Fail
0.0.96.128.6.255 | - | Manufacturer specific | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.128.7.255 | - | Manufacturer specific | 5 | 32-bit signed integer | - | Not found | - | - | - | - | - | Fail
0.0.96.128.8.255 | - | Manufacturer specific | 2 | Structure from data of different types | - | Not found | - | - | - | - | - | Fail
0.0.96.135.0.255 | - | Manufacturer specific | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.96.135.1.255 | - | Manufacturer specific | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.97.97.0.255 | - | Ch. 0 Error object #1 | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.97.98.0.255 | Текущее состояние инициативного выхода | Ch. 0 Alarm register object #1 | 6 | 32-bit unsigned integer | - | Ch. 0 Alarm register object #1 | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.97.98.1.255 | - | Ch. 0 Alarm register object #2 | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.97.98.4.255 | - | Ch. 0 Alarm register object #5 | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.97.98.5.255 | - | Ch. 0 Alarm register object #6 | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.97.98.6.255 | - | Ch. 0 Alarm register object #7 | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.97.98.10.255 | Фильтр событий инициативного выхода | Ch. 0 Alarm filter object #1 | 6 | 32-bit unsigned integer | - | Ch. 0 Alarm filter object #1 | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.97.98.11.255 | Фильтр событий отключения реле нагрузки | Ch. 0 Alarm filter object #2 | 6 | 32-bit unsigned integer | - | Ch. 0 Alarm filter object #2 | 18 | 16-bit unsigned integer | - | Yes | No | Fail
0.0.97.98.20.255 | Сброс событий инициативного выхода | Ch. 0 Alarm descriptor object #11 | 6 | 32-bit unsigned integer | - | Ch. 0 Alarm descriptor object #11 | 6 | 32-bit unsigned integer | - | Yes | Yes | Success
0.0.97.98.21.255 | - | Ch. 0 Alarm descriptor object #12 | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.0.128.1.0.255 | Часы больших нагрузок | Manufacturer specific | 2 | Structure from data of different types | - | Manufacturer specific | 0 | Missing data | - | Yes | No | Fail
0.0.128.2.0.255 | Часы утреннего и вечернего максимума | Manufacturer specific | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.0.135.210.0.255 | Настройка коммуникационного профиля для портов связи | Manufacturer specific | 17 | 8-bit unsigned integer | - | Manufacturer specific | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
0.0.135.210.2.255 | - | Manufacturer specific | 9 | Byte sequence | - | Manufacturer specific | 9 | Byte sequence | - | Yes | Yes | Success
0.0.135.220.0.255 | Настройка учёта энергии | Manufacturer specific | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.1.94.14.105.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.106.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.107.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.108.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.109.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.110.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.111.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.112.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.113.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.114.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.115.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.116.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.117.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.118.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.14.119.255 | - | Ch. 1 Identifiers for Israel | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.31.0.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.1.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.2.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.3.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.4.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.5.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.6.255 | - | Ch. 1 Identifiers for the Netherlands | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.7.255 | - | Ch. 1 Identifiers for the Netherlands | 16 | 16-bit signed integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.8.255 | - | Ch. 1 Identifiers for the Netherlands | 15 | 8-bit signed integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.9.255 | - | Ch. 1 Identifiers for the Netherlands | 15 | 8-bit signed integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.10.255 | - | Ch. 1 Identifiers for the Netherlands | 15 | 8-bit signed integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.11.255 | - | Ch. 1 Identifiers for the Netherlands | 16 | 16-bit signed integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.12.255 | - | Ch. 1 Identifiers for the Netherlands | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.13.255 | - | Ch. 1 Identifiers for the Netherlands | 16 | 16-bit signed integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.14.255 | - | Ch. 1 Identifiers for the Netherlands | 18 | 16-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.15.255 | - | Ch. 1 Identifiers for the Netherlands | 18 | 16-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.16.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.17.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.18.255 | - | Ch. 1 Identifiers for the Netherlands | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
0.1.94.31.19.255 | - | Ch. 1 Identifiers for the Netherlands | 1 | Array of homogeneous data | - | Not found | - | - | - | - | - | Fail
0.1.94.31.20.255 | - | Ch. 1 Identifiers for the Netherlands | 0 | Missing data | - | Not found | - | - | - | - | - | Fail
0.1.94.31.21.255 | - | Ch. 1 Identifiers for the Netherlands | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
0.1.94.31.22.255 | - | Ch. 1 Identifiers for the Netherlands | 2 | Structure from data of different types | - | Not found | - | - | - | - | - | Fail
0.1.94.31.23.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.24.255 | - | Ch. 1 Identifiers for the Netherlands | 2 | Structure from data of different types | - | Not found | - | - | - | - | - | Fail
0.1.94.31.25.255 | - | Ch. 1 Identifiers for the Netherlands | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
0.1.94.31.26.255 | - | Ch. 1 Identifiers for the Netherlands | 18 | 16-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
0.1.94.31.27.255 | - | Ch. 1 Identifiers for the Netherlands | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.1.94.31.28.255 | - | Ch. 1 Identifiers for the Netherlands | 0 | Missing data | - | Not found | - | - | - | - | - | Fail
1.0.0.2.0.255 | - | Ch. 0 Active firmware identifier | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
1.0.0.2.8.255 | - | Ch. 0 Active firmware signature | 9 | Byte sequence | - | Ch. 0 Active firmware signature | 9 | Byte sequence | - | Yes | Yes | Success
1.0.0.3.3.255 | Постоянная счетчика для активной энергии | Ch. 0 Meter constant Active energy, output pulse | 18 | 16-bit unsigned integer | - | Ch. 0 Meter constant Active energy, output pulse | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
1.0.0.3.4.255 | Постоянная счетчика для реактивной энергии | Ch. 0 Meter constant Reactive energy, output pulse | 18 | 16-bit unsigned integer | - | Ch. 0 Meter constant Reactive energy, output pulse | 18 | 16-bit unsigned integer | - | Yes | Yes | Success
1.0.0.3.128.255 | - | Man. specific | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
1.0.0.3.129.255 | - | Man. specific | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
1.0.0.8.4.255 | Период записи в профиль 1 (энергия на интервале) | Ch. 0 Recording interval 1, for load profile | 17 | 8-bit unsigned integer | - | Ch. 0 Recording interval 1, for load profile | 17 | 8-bit unsigned integer | - | Yes | Yes | Success
1.0.0.8.5.255 | Интервал интегрирования 2 параметров сети | Ch. 0 Recording interval 2, for load profile | 17 | 8-bit unsigned integer | - | Ch. 0 Recording interval 2, for load profile | 0 | Missing data | - | Yes | No | Fail
1.0.0.9.1.255 | - | Ch. 0 Local time | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
1.0.0.9.2.255 | - | Ch. 0 Local date | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
1.0.0.10.2.255 | Активное сопротивление линии | Invalid | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
1.0.0.11.1.255 | - | Ch. 0 Measurement algorithm Active power | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
1.0.0.11.2.255 | - | Ch. 0 Measurement algorithm Active energy | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
1.0.0.11.3.255 | - | Ch. 0 Measurement algorithm Reactive power | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
1.0.0.11.4.255 | - | Ch. 0 Measurement algorithm Reactive energy | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
1.0.0.11.5.255 | - | Ch. 0 Measurement algorithm Apparent power | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
1.0.0.11.6.255 | - | Ch. 0 Measurement algorithm Apparent energy | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
1.0.0.11.7.255 | - | Ch. 0 Measurement algorithm Power factor calculation | 22 | Enumeration | - | Not found | - | - | - | - | - | Fail
1.0.32.32.0.255 | - | Ch. 0 L1 Voltage Unipede voltage dip Class 10...<= 15%, 10ms...<= 100ms | 18 | 16-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
1.0.32.36.0.255 | - | Ch. 0 L1 Voltage Over limit occurrence counter Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
1.0.32.40.0.255 | - | Ch. 0 L1 Voltage Missing occurrence counter Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
1.0.94.98.69.255 | - | Ch. 0 Identifiers for Iran | 0 | Missing data | - | Not found | - | - | - | - | - | Fail
1.0.96.0.142.255 | - | Man. specific | 3 | Logical data (TRUE, FALSE) | - | Not found | - | - | - | - | - | Fail
1.0.128.128.0.255 | - | Man. specific | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
1.0.128.128.1.255 | - | Man. specific | 6 | 32-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
1.1.0.2.0.255 | - | Ch. 1 Active firmware identifier | 9 | Byte sequence | - | Ch. 1 Active firmware identifier | 9 | Byte sequence | - | Yes | Yes | Success
1.1.94.14.100.255 | - | Ch. 1 Identifiers for Israel | 17 | 8-bit unsigned integer | - | Not found | - | - | - | - | - | Fail
1.2.0.2.8.255 | - | Ch. 2 Active firmware signature | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
1.4.0.2.0.255 | - | Ch. 4 Active firmware identifier | 9 | Byte sequence | - | Not found | - | - | - | - | - | Fail
0.0.96.6.3.255 | - | Ch. 0 Battery voltage | 18 | 16-bit unsigned integer | 0.01 | Ch. 0 Battery voltage | 18 | 16-bit unsigned integer | 0.01 | Yes | Yes | Success
0.0.96.7.19.255 | - | Ch. 0 Duration of long power failure in any phase | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
0.0.96.7.20.255 | - | Ch. 0 Time threshold for long of power failure | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
0.0.96.7.128.255 | - | Manufacturer specific | 18 | 16-bit unsigned integer | 0.01 | Not found | - | - | - | - | - | Fail
0.0.96.8.0.255 | Время работы счетчика | Ch. 0 Time of operation, total | 6 | 32-bit unsigned integer | 1 | Ch. 0 Time of operation, total | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
0.0.96.9.0.255 | Температура внутри корпуса ПУ | Ch. 0 Ambient temperature | 16 | 16-bit signed integer | 0.1 | Ch. 0 Ambient temperature | 16 | 16-bit signed integer | 0.1 | Yes | Yes | Success
0.0.96.35.0.255 | - | Invalid | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
0.0.96.44.0.255 | - | Invalid | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
0.96.128.35.0.255 | - | Ch. 96 Utility specific objects | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.0.6.0.255 | Номинальное напряжение | Ch. 0 Nominal voltage | 18 | 16-bit unsigned integer | 0.1 | Ch. 0 Nominal voltage | 18 | 16-bit unsigned integer | 0.1 | Yes | Yes | Success
1.0.0.6.1.255 | Номинальный ток | Ch. 0 Basic/nominal current | 18 | 16-bit unsigned integer | 1 | Ch. 0 Basic/nominal current | 18 | 16-bit unsigned integer | 0.1 | No | Yes | Fail
1.0.0.6.2.255 | Номинальное частота | Ch. 0 Nominal frequency | 18 | 16-bit unsigned integer | 1 | Ch. 0 Nominal frequency | 17 | 8-bit unsigned integer | 1 | Yes | No | Fail
1.0.0.6.3.255 | Максимальный ток | Ch. 0 Maximum current | 18 | 16-bit unsigned integer | 1 | Ch. 0 Maximum current | 18 | 16-bit unsigned integer | 0.1 | No | Yes | Fail
1.0.0.6.4.255 | Согласованное напряжение электропитания | Ch. 0 Reference voltage for power quality measurement | 18 | 16-bit unsigned integer | 1 | Ch. 0 Reference voltage for power quality measurement | 6 | 32-bit unsigned integer | 0.001 | No | No | Fail
1.0.0.9.11.255 | - | Ch. 0 Clock time shift limit | 17 | 8-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.7.0.255 | Суммарная активная мощность | Ch. 0 Sum Li Active power+ (QI+QIV) Inst. value | 5 | 32-bit signed integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Inst. value | 5 | 32-bit signed integer | 0.001 | No | Yes | Fail
1.0.1.8.0.101 | Активная энергия нарастающим итогом, импорт. Сумма по тарифам | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.0.102 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 0 (0 is total) 2. last / 2 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.0.103 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 0 (0 is total) 3. last / 3 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.0.255 | Активная энергия, импорт | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.1.101 | Активная энергия нарастающим итогом, импорт. Тариф 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.1.102 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 1 (0 is total) 2. last / 2 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.1.103 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 1 (0 is total) 3. last / 3 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.1.255 | Активная энергия, импорт по 1 тарифу | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.2.101 | Активная энергия нарастающим итогом, импорт. Тариф 2 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.2.102 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 2 (0 is total) 2. last / 2 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.2.103 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 2 (0 is total) 3. last / 3 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.2.255 | Активная энергия, импорт по 2 тарифу | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.3.101 | Активная энергия нарастающим итогом, импорт. Тариф 3 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.3.102 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 3 (0 is total) 2. last / 2 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.3.103 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 3 (0 is total) 3. last / 3 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.3.255 | Активная энергия, импорт по 3 тарифу | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.4.101 | Активная энергия нарастающим итогом, импорт. Тариф 4 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.8.4.102 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 4 (0 is total) 2. last / 2 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.4.103 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 4 (0 is total) 3. last / 3 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.8.4.255 | Активная энергия, импорт по 4 тарифу | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.9.0.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 2 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.9.1.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 2 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.9.2.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 2 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.9.3.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 2 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.9.4.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 2 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.29.0.255 | Активная энергия, импорт за период записи | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 5 | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 5 | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.1.35.0.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Over limit threshold Rate 0 (0 is total) Threshold 255 | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.7.0.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Inst. value | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.8.0.101 | Активная энергия нарастающим итогом, экспорт. Сумма по тарифам | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.0.255 | Активная энергия, экспорт | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.1.101 | Активная энергия нарастающим итогом, экспорт. Тариф 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.1.255 | Активная энергия, экспорт по 1 тарифу | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.2.101 | Активная энергия нарастающим итогом, экспорт. Тариф 2 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.2.255 | Активная энергия, экспорт по 2 тарифу | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.3.101 | Активная энергия нарастающим итогом, экспорт. Тариф 3 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.3.255 | Активная энергия, экспорт по 3 тарифу | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.4.101 | Активная энергия нарастающим итогом, экспорт. Тариф 4 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.8.4.255 | Активная энергия, экспорт по 4 тарифу | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.2.9.0.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 2 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.9.1.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 2 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.9.2.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 2 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.9.3.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 2 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.9.4.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 2 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.29.0.255 | Активная энергия, экспорт за период записи | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 5 | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 5 | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.7.0.255 | Суммарная реактивная мощность | Ch. 0 Sum Li Reactive power+ (QI+QII) Inst. value | 5 | 32-bit signed integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Inst. value | 5 | 32-bit signed integer | 0.001 | No | Yes | Fail
1.0.3.8.0.101 | Реактивная энергия нарастающим итогом, импорт. Сумма по тарифам | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.0.255 | Реактивная энергия, импорт | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.1.101 | Реактивная энергия нарастающим итогом, импорт. Тариф 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.1.255 | Реактивная энергия, импорт по 1 тарифу | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.2.101 | Реактивная энергия нарастающим итогом, импорт. Тариф 2 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.2.255 | Реактивная энергия, импорт по 2 тарифу | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.3.101 | Реактивная энергия нарастающим итогом, импорт. Тариф 3 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.3.255 | Реактивная энергия, импорт по 3 тарифу | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.4.101 | Реактивная энергия нарастающим итогом, импорт. Тариф 4 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.8.4.255 | Реактивная энергия, импорт по 4 тарифу | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.3.9.0.255 | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 2 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.3.9.1.255 | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 2 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.3.9.2.255 | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 2 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.3.9.3.255 | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 2 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.3.9.4.255 | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 2 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.3.29.0.255 | Реактивная энергия, импорт, за период записи | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 5 | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 5 | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.7.0.255 | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Inst. value | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.4.8.0.101 | Реактивная энергия нарастающим итогом, экспорт. Сумма по тарифам | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.0.255 | Реактивная энергия, экспорт | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.1.101 | Реактивная энергия нарастающим итогом, экспорт. Тариф 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.1.255 | Реактивная энергия, экспорт по 1 тарифу | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.2.101 | Реактивная энергия нарастающим итогом, экспорт. Тариф 2 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.2.255 | Реактивная энергия, экспорт по 2 тарифу | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.3.101 | Реактивная энергия нарастающим итогом, экспорт. Тариф 3 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.3.255 | Реактивная энергия, экспорт по 3 тарифу | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.4.101 | Реактивная энергия нарастающим итогом, экспорт. Тариф 4 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.8.4.255 | Реактивная энергия, экспорт по 4 тарифу | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.4.9.0.255 | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 2 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.4.9.1.255 | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 2 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.4.9.2.255 | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 2 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.4.9.3.255 | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 2 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.4.9.4.255 | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 2 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.4.29.0.255 | Реактивная энергия, экспорт, за период записи | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 5 | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 5 | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.9.3.128.255 | Минимальное значение полной мощности на интервале интегрирования 2 за расчетный период | Man. specific | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.9.6.128.255 | Максимальное значение полной мощности на интервале интегрирования 2 за расчетный период | Man. specific | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.9.7.0.255 | Суммарная полная мощность | Ch. 0 Sum Li Apparent power+ (QI+QIV) Inst. value | 5 | 32-bit signed integer | 1 | Ch. 0 Sum Li Apparent power+ (QI+QIV) Inst. value | 6 | 32-bit unsigned integer | 0.001 | No | No | Fail
1.0.10.7.0.255 | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Inst. value | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.11.7.0.255 | Ток I | Ch. 0 Current: any phase Inst. value | 6 | 32-bit unsigned integer | 0.001 | Ch. 0 Current: any phase Inst. value | 5 | 32-bit signed integer | 0.001 | Yes | No | Fail
1.0.11.35.3.255 | - | Ch. 0 Current: any phase Over limit threshold Harmonic / Distortion factor 3 Threshold 255 | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.11.44.0.255 | - | Ch. 0 Current: any phase Time threshold for over limit Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.11.134.0.255 | Ток | Man. specific | 17 | 8-bit unsigned integer | 0.01 | Man. specific | 18 | 16-bit unsigned integer | 1 | No | No | Fail
1.0.12.7.0.255 | Напряжение U | Ch. 0 Voltage: any phase Inst. value | 18 | 16-bit unsigned integer | 0.1 | Ch. 0 Voltage: any phase Inst. value | 6 | 32-bit unsigned integer | 0.001 | No | No | Fail
1.0.12.7.4.255 | Глубина провала/ перенапряжения | Ch. 0 Voltage: any phase Inst. value Harmonic 4 | 18 | 16-bit unsigned integer | 0.1 | Ch. 0 Voltage: any phase Inst. value Harmonic 4 | 6 | 32-bit unsigned integer | 0.001 | No | No | Fail
1.0.12.31.0.255 | Порог для фиксации провала напряжения | Ch. 0 Voltage: any phase Under limit threshold Harmonic / Distortion factor 0 Threshold 255 | 18 | 16-bit unsigned integer | 1 | Ch. 0 Voltage: any phase Under limit threshold Harmonic / Distortion factor 0 Threshold 255 | 6 | 32-bit unsigned integer | 0.001 | No | No | Fail
1.0.12.35.0.255 | Порог для фиксации перенапряжения | Ch. 0 Voltage: any phase Over limit threshold Harmonic / Distortion factor 0 Threshold 255 | 18 | 16-bit unsigned integer | 1 | Ch. 0 Voltage: any phase Over limit threshold Harmonic / Distortion factor 0 Threshold 255 | 6 | 32-bit unsigned integer | 0.001 | No | No | Fail
1.0.12.39.0.255 | Пороговое напряжение для фиксации перерыва питания | Ch. 0 Voltage: any phase Missing threshold Harmonic / Distortion factor 0 Threshold 255 | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.12.43.0.255 | - | Ch. 0 Voltage: any phase Time threshold for under limit Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | 1 | Ch. 0 Voltage: any phase Time threshold for under limit Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | 1 | Yes | Yes | Success
1.0.12.44.0.255 | - | Ch. 0 Voltage: any phase Time threshold for over limit Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | 1 | Ch. 0 Voltage: any phase Time threshold for over limit Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | 1 | Yes | Yes | Success
1.0.12.45.0.255 | - | Ch. 0 Voltage: any phase Time threshold of missing magnitude Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | 1 | Ch. 0 Voltage: any phase Time threshold of missing magnitude Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 0 | Missing data | 1 | Yes | No | Fail
1.0.12.128.0.255 | Положительное отклонение напряжения, в % (для однофазных ПУ) | Man. specific | 18 | 16-bit unsigned integer | 0.01 | Man. specific | 6 | 32-bit unsigned integer | 0.1 | No | No | Fail
1.0.12.129.0.255 | Отрицательное отклонение напряжения, в % (для однофазных ПУ) | Man. specific | 18 | 16-bit unsigned integer | 0.01 | Man. specific | 6 | 32-bit unsigned integer | 0.1 | No | No | Fail
1.0.12.134.0.255 | Напряжение | Man. specific | 17 | 8-bit unsigned integer | 0.01 | Man. specific | 18 | 16-bit unsigned integer | 1 | No | No | Fail
1.0.13.7.0.255 | Суммарный коэф. мощности | Ch. 0 Sum Li Power factor Inst. value | 16 | 16-bit signed integer | 0.001 | Ch. 0 Sum Li Power factor Inst. value | 5 | 32-bit signed integer | 0.0001 | No | No | Fail
1.0.14.7.0.255 | Частота сети F | Ch. 0 Supply frequency Inst. value | 18 | 16-bit unsigned integer | 0.01 | Ch. 0 Supply frequency Inst. value | 6 | 32-bit unsigned integer | 0.001 | No | No | Fail
1.0.14.130.0.255 | Установившееся отклонение частоты, Гц | Man. specific | 16 | 16-bit signed integer | 0.01 | Man. specific | 5 | 32-bit signed integer | 0.001 | No | No | Fail
1.0.15.3.128.255 | Минимальное значение активной мощности на интервале интегрирования 2 за расчетный период | Man. specific | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.6.128.255 | Максимальное значение активной мощности на интервале интегрирования 2 за расчетный период | Man. specific | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.6.129.255 | Усредненное за месяц суточное значение максимальной активной мощности на интервале интегрирования 2 | Man. specific | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.6.130.255 | Усредненное за месяц суточное значение максимальной активной мощности на интервале интегрирования 2 в период пиковых нагрузок | Man. specific | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.7.0.255 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Inst. value | 6 | 32-bit unsigned integer | 1 | - | - | - | - | No | No | Fail
1.0.15.8.0.101 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 0 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.8.0.255 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.15.8.1.101 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 1 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.8.1.255 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.15.8.2.101 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 2 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.8.2.255 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.15.8.3.101 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 3 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.8.3.255 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.15.8.4.101 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 4 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.8.4.255 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.15.16.0.255 | Суточное значение максимальной активной мощности на интервале интегрирования 2 | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Max. 2 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.16.1.255 | Суточное значение максимальной активной мощности на интервале интегрирования 2 в период пиковых нагрузок | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Max. 2 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.15.35.128.255 | Максимальное значение активной мощности на интервале интегрирования 2 за расчетный период. Пороговое значение | Man. specific | 6 | 32-bit unsigned integer | 1 | Man. specific | 0 | Missing data | 0.001 | No | No | Fail
1.0.15.35.130.255 | Максимальное значение активной мощности на интервале интегрирования 2 за расчетный период в период пиковых нагрузок. Пороговое значение | Man. specific | 6 | 32-bit unsigned integer | 1 | Man. specific | 0 | Missing data | 0.001 | No | No | Fail
1.0.16.7.0.255 | - | Ch. 0 Sum Li Active power (abs(QI+QIV)-abs(QII+QIII)) Inst. value | 5 | 32-bit signed integer | 1 | Not found | - | - | - | - | - | Fail
1.0.31.23.0.255 | - | Ch. 0 L1 Current Min. 3 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 0.001 | Not found | - | - | - | - | - | Fail
1.0.31.24.0.255 | - | Ch. 0 L1 Current Current avg. 3 | 6 | 32-bit unsigned integer | 0.001 | Not found | - | - | - | - | - | Fail
1.0.31.25.0.255 | - | Ch. 0 L1 Current Last avg. 3 | 6 | 32-bit unsigned integer | 0.001 | Not found | - | - | - | - | - | Fail
1.0.31.26.0.255 | - | Ch. 0 L1 Current Max. 3 | 6 | 32-bit unsigned integer | 0.001 | Not found | - | - | - | - | - | Fail
1.0.32.23.0.255 | - | Ch. 0 L1 Voltage Min. 3 Rate 0 (0 is total) | 18 | 16-bit unsigned integer | 0.1 | Not found | - | - | - | - | - | Fail
1.0.32.24.0.255 | - | Ch. 0 L1 Voltage Current avg. 3 | 18 | 16-bit unsigned integer | 0.1 | Not found | - | - | - | - | - | Fail
1.0.32.25.0.255 | - | Ch. 0 L1 Voltage Last avg. 3 | 18 | 16-bit unsigned integer | 0.1 | Not found | - | - | - | - | - | Fail
1.0.32.26.0.255 | - | Ch. 0 L1 Voltage Max. 3 | 18 | 16-bit unsigned integer | 0.1 | Not found | - | - | - | - | - | Fail
1.0.32.33.0.255 | - | Ch. 0 L1 Voltage Under limit duration Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.32.34.0.255 | - | Ch. 0 L1 Voltage Under limit magnitude Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.32.37.0.255 | - | Ch. 0 L1 Voltage Over limit duration Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.32.38.0.255 | - | Ch. 0 L1 Voltage Over limit magnitude Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.32.41.0.255 | - | Ch. 0 L1 Voltage Missing duration Harmonic / Distortion factor 0 Billing period 255 (255 is current) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.81.7.4.255 | Угол UI фазы A | Ch. 0 Angle of I(L1) - U(L1) | 18 | 16-bit unsigned integer | 0.1 | Ch. 0 Angle of I(L1) - U(L1) | 16 | 16-bit signed integer | 1 | No | No | Fail
1.0.88.8.0.255 | Удельная энергия потерь в ЛЭП | Ch. 0 Sum Li A2h QI+QII+QIII+QIV Time integral 1 Rate 0 (0 is total) | 21 | 64-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.91.7.0.255 | Ток I0 | Ch. 0 Lo Current (neutral) Inst. value | 6 | 32-bit unsigned integer | 0.001 | Ch. 0 Lo Current (neutral) Inst. value | 5 | 32-bit signed integer | 0.001 | Yes | No | Fail
1.0.91.7.131.255 | Диф. Ток | Man. specific | 6 | 32-bit unsigned integer | 0.001 | Man. specific | 5 | 32-bit signed integer | 0.001 | Yes | No | Fail
1.0.91.7.132.255 | Диф. Ток, % | Man. specific | 18 | 16-bit unsigned integer | 1 | Man. specific | 6 | 32-bit unsigned integer | 0.1 | No | No | Fail
1.0.128.44.0.255 | - | Man. specific | 18 | 16-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.131.6.128.255 | Коэффициент реактивной мощности tg (φ). Максимальное значение на интервале интегрирования 2 за расчетный период | Man. specific | 6 | 32-bit unsigned integer | 0.001 | Not found | - | - | - | - | - | Fail
1.0.131.7.0.255 | Суммарный коэффициент реактивной мощности | Man. specific | 6 | 32-bit unsigned integer | 0.001 | Man. specific | 5 | 32-bit signed integer | 0.0001 | No | No | Fail
1.0.131.27.0.255 | Коэффициент реактивной мощности tg (φ). Среднее значение на интервале интегрирования. | Man. specific | 6 | 32-bit unsigned integer | 0.001 | Man. specific | 5 | 32-bit signed integer | 0.0001 | No | No | Fail
1.0.131.35.0.255 | Коэффициент реактивной мощности (tg φ) средний по всем фазам. Пороговое значение | Man. specific | 18 | 16-bit unsigned integer | 1 | Man. specific | 5 | 32-bit signed integer | 0.0001 | No | No | Fail
1.0.131.44.0.255 | Коэффициент реактивной мощности (tg φ) средний по всем фазам. Пороговое значение по времени | Man. specific | 17 | 8-bit unsigned integer | 1 | Man. specific | 17 | 8-bit unsigned integer | 1 | Yes | Yes | Success
1.0.137.3.128.255 | Минимальное значение реактивной мощности на интервале интегрирования 2 за расчетный период | Man. specific | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.137.6.128.255 | Максимальное значение реактивной мощности на интервале интегрирования 2 за расчетный период | Man. specific | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.145.35.0.255 | Порог отклонения частоты, Гц | Man. specific | 18 | 16-bit unsigned integer | 0.1 | Man. specific | 6 | 32-bit unsigned integer | 0.001 | No | No | Fail
1.0.147.133.0.255 | Суммарное время отклонения напряжения за расчётный период | Man. specific | 6 | 32-bit unsigned integer | 1 | Man. specific | 6 | 32-bit unsigned integer | 1 | Yes | Yes | Success
1.0.148.36.0.255 | Количество перенапряжений за расчётный период | Man. specific | 6 | 32-bit unsigned integer | 1 | Man. specific | 6 | 32-bit unsigned integer | - | No | Yes | Fail
1.0.150.7.0.255 | - | Man. specific | 5 | 32-bit signed integer | 0.001 | Man. specific | 5 | 32-bit signed integer | 0.0001 | No | Yes | Fail
1.0.1.6.0.255 | Максимальная мощность на расчётном периоде и дата время начала интервала максимальной мощности | Ch. 0 Sum Li Active power+ (QI+QIV) Max. 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.6.1.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Max. 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.6.2.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Max. 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.6.3.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Max. 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.6.4.255 | - | Ch. 0 Sum Li Active power+ (QI+QIV) Max. 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.6.0.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Max. 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.6.1.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Max. 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.6.2.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Max. 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.6.3.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Max. 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.2.6.4.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Max. 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | Not found | - | - | - | - | - | Fail
1.0.1.4.0.255 | Период интегрирования максимальной мощности | Ch. 0 Sum Li Active power+ (QI+QIV) Current avg. 1 Rate 0 (0 is total) | - | - | 1 | Ch. 0 Sum Li Active power+ (QI+QIV) Current avg. 1 Rate 0 (0 is total) | - | - | 0.001 | No | Yes | Fail
1.0.2.4.0.255 | - | Ch. 0 Sum Li Active power- (QII+QIII) Current avg. 1 Rate 0 (0 is total) | - | - | 1 | Not found | - | - | - | - | - | Fail
0.0.14.0.1.255 | - | Ch. 0 Register activation #2 | - | - | - | Ch. 0 Register activation #2 | - | - | - | Yes | Yes | Success
0.0.21.0.1.255 | Список отображаемых на дисплее объектов в режиме «Автопрокрутка» | Ch. 0 General display readout | - | - | - | Ch. 0 General display readout | - | - | - | Yes | Yes | Success
0.0.1.0.0.255 | Дата и время захвата | Ch. 0 Clock object #1 | - | - | - | Ch. 0 Clock object #1 | - | - | - | Yes | Yes | Success
0.0.21.0.2.255 | Список отображаемых на дисплее объектов в режиме «По кнопке» | Ch. 0 Alternate display readout | - | - | - | Ch. 0 Alternate display readout | - | - | - | Yes | Yes | Success
0.0.94.7.1.255 | Список захватываемых объектов: | Ch. 0 Identifiers for Russia | - | - | - | Ch. 0 Identifiers for Russia | - | - | - | Yes | Yes | Success
0.0.99.98.0.255 | Напряжений | Ch. 0 Event log #1 | - | - | - | Ch. 0 Event log #1 | - | - | - | Yes | Yes | Success
0.0.99.98.1.255 | Токов | Ch. 0 Event log #2 | - | - | - | Ch. 0 Event log #2 | - | - | - | Yes | Yes | Success
0.0.99.98.2.255 | Включений/ выключений | Ch. 0 Event log #3 | - | - | - | Ch. 0 Event log #3 | - | - | - | Yes | Yes | Success
0.0.99.98.3.255 | Коррекций данных | Ch. 0 Event log #4 | - | - | - | Ch. 0 Event log #4 | - | - | - | Yes | Yes | Success
0.0.99.98.4.255 | Внешних воздействий | Ch. 0 Event log #5 | - | - | - | Ch. 0 Event log #5 | - | - | - | Yes | Yes | Success
0.0.99.98.5.255 | Коммуникационные события | Ch. 0 Event log #6 | - | - | - | Ch. 0 Event log #6 | - | - | - | Yes | Yes | Success
0.0.99.98.6.255 | Контроль доступа | Ch. 0 Event log #7 | - | - | - | Ch. 0 Event log #7 | - | - | - | Yes | Yes | Success
0.0.99.98.7.255 | Самодиагностики | Ch. 0 Event log #8 | - | - | - | Ch. 0 Event log #8 | - | - | - | Yes | Yes | Success
0.0.99.98.8.255 | Превышение тангенса | Ch. 0 Event log #9 | - | - | - | Ch. 0 Event log #9 | - | - | - | Yes | Yes | Success
0.0.99.98.9.255 | Параметры качества сети | Ch. 0 Event log #10 | - | - | - | Ch. 0 Event log #10 | - | - | - | Yes | Yes | Success
0.0.99.98.12.255 | Выход тангенса за порог на интервале интегрирования | Ch. 0 Event log #13 | - | - | - | Ch. 0 Event log #13 | - | - | - | Yes | Yes | Success
0.0.99.98.13.255 | Коррекции времени | Ch. 0 Event log #14 | - | - | - | Ch. 0 Event log #14 | - | - | - | Yes | Yes | Success
0.0.1.0.1.255 | Старое время | Ch. 0 Clock object, nth instance #2 | - | - | - | Ch. 0 Clock object, nth instance #2 | - | - | - | Yes | Yes | Success
0.0.99.98.14.255 | Годовой профиль | Ch. 0 Event log #15 | - | - | - | Not found | - | - | - | - | - | Fail
0.0.99.98.15.255 | Качества сети на расчётный период | Ch. 0 Event log #16 | - | - | - | Ch. 0 Event log #16 | - | - | - | Yes | Yes | Success
0.0.99.98.16.255 | Контроль мощности | Ch. 0 Event log #17 | - | - | - | Ch. 0 Event log #17 | - | - | - | Yes | Yes | Success
0.0.99.98.18.255 | Контроль блокиратора реле нагрузки | Ch. 0 Event log #19 | - | - | - | Ch. 0 Event log #19 | - | - | - | Yes | Yes | Success
0.0.99.98.101.255 | - | Ch. 0 Event log #102 | - | - | - | Not found | - | - | - | - | - | Fail
0.0.96.11.14.255 | - | - | - | - | - | Not found | - | - | - | - | - | Fail
1.3.0.0.0.255 | - | - | - | - | - | Not found | - | - | - | - | - | Fail
1.0.94.7.0.255 | Текущие значения | Ch. 0 Identifiers for Russia | - | - | - | Ch. 0 Identifiers for Russia | - | - | - | Yes | Yes | Success
1.0.94.7.1.255 | Профиль масштаба для журнала ежемесячных показаний | Ch. 0 Identifiers for Russia | - | - | - | Ch. 0 Identifiers for Russia | - | - | - | Yes | Yes | Success
1.0.94.7.2.255 | Профиль масштаба для журнала ежесуточных показаний | Ch. 0 Identifiers for Russia | - | - | - | Ch. 0 Identifiers for Russia | - | - | - | Yes | Yes | Success
1.0.94.7.3.255 | Профиль масштаба для стоп-кадра текущих значений | Ch. 0 Identifiers for Russia | - | - | - | Ch. 0 Identifiers for Russia | - | - | - | Yes | Yes | Success
1.0.94.7.4.255 | Профиль масштаба для профилей нагрузки | Ch. 0 Identifiers for Russia | - | - | - | Ch. 0 Identifiers for Russia | - | - | - | Yes | Yes | Success
1.0.94.7.5.255 | Профиль телеизмерений для задач телемеханики | Ch. 0 Identifiers for Russia | - | - | - | Not found | - | - | - | - | - | Fail
1.0.98.1.0.255 | Месячный | Ch. 0 Data of billing period Scheme 1 #1 Unspecified number of most recent billing periods | - | - | - | Ch. 0 Data of billing period Scheme 1 #1 Unspecified number of most recent billing periods | - | - | - | Yes | Yes | Success
1.0.98.2.0.255 | Суточный | Ch. 0 Data of billing period Scheme 2 #1 Unspecified number of most recent billing periods | - | - | - | Ch. 0 Data of billing period Scheme 2 #1 Unspecified number of most recent billing periods | - | - | - | Yes | Yes | Success
1.0.99.1.0.255 | Нагрузки | Ch. 0 Load profile with recording period 1 #1 | - | - | - | Ch. 0 Load profile with recording period 1 #1 | - | - | - | Yes | Yes | Success
1.0.99.2.0.255 | Часовой профиль | Ch. 0 Load profile with recording period 2 #1 | - | - | - | Not found | - | - | - | - | - | Fail
0.0.10.0.1.255 | Конец расчетного периода | Ch. 0 MDI reset / End of billing period | - | - | - | Ch. 0 MDI reset / End of billing period | - | - | - | Yes | Yes | Success
0.0.10.0.100.255 | - | Ch. 0 Tariffication script table | - | - | - | Ch. 0 Tariffication script table | - | - | - | Yes | Yes | Success
0.0.10.0.103.255 | - | Ch. 0 Set output signals | - | - | - | Ch. 0 Set output signals | - | - | - | Yes | Yes | Success
0.0.10.0.106.255 | Реле нагрузки | Ch. 0 Disconnect control | - | - | - | Ch. 0 Disconnect control | - | - | - | Yes | Yes | Success
0.0.96.3.10.255 | Настройка | Ch. 0 Disconnect control | - | - | - | Ch. 0 Disconnect control | - | - | - | Yes | Yes | Success
0.0.10.0.107.255 | - | Ch. 0 Image activation | - | - | - | Ch. 0 Image activation | - | - | - | Yes | Yes | Success
0.0.44.0.0.255 | - | Ch. 0 Image transfer #0 | - | - | - | Ch. 0 Image transfer #0 | - | - | - | Yes | Yes | Success
0.0.10.0.108.255 | - | Ch. 0 Push script table | - | - | - | Ch. 0 Push script table | - | - | - | Yes | Yes | Success
0.0.25.9.0.255 | Настройка PUSH | Ch. 0 Push setup | - | - | - | Ch. 0 Push setup | - | - | - | Yes | Yes | Success
0.0.10.0.109.255 | - | Ch. 0 Load profile control script table | - | - | - | Not found | - | - | - | - | - | Fail
0.0.17.0.0.255 | Активная мощность | Ch. 0 Limiter #1 | - | - | - | Ch. 0 Limiter #1 | - | - | - | Yes | Yes | Success
0.0.10.0.128.255 | - | Manufacturer specific | - | - | - | Not found | - | - | - | - | - | Fail
0.2.10.0.1.255 | - | Ch. 2 MDI reset / End of billing period | - | - | - | Not found | - | - | - | - | - | Fail
0.0.11.0.0.255 | Исключительные дни | Ch. 0 Special days table #1 | - | - | - | Ch. 0 Special days table #1 | - | - | - | Yes | Yes | Success
0.0.40.0.0.255 | Объект текущего соединения | Ch. 0 Current association | - | - | - | Ch. 0 Current association | - | - | - | Yes | Yes | Success
0.0.41.0.0.255 | SAP Assignment | Ch. 0 SAP Assignment | - | - | - | Ch. 0 SAP Assignment | - | - | - | Yes | Yes | Success
0.0.20.0.0.255 | Настройка IEC | Ch. 0 IEC optical port setup | - | - | - | Ch. 0 IEC optical port setup | - | - | - | Yes | Yes | Success
0.0.13.0.0.255 | Календарь | Ch. 0 Activity calendar #1 | - | - | - | Ch. 0 Activity calendar #1 | - | - | - | Yes | Yes | Success
0.0.16.1.0.255 | - | Ch. 0 Alarm monitor #1 | - | - | - | Not found | - | - | - | - | - | Fail
0.0.16.1.1.255 | Монитор событий реле нагрузки | Ch. 0 Alarm monitor #2 | - | - | - | Not found | - | - | - | - | - | Fail
0.0.15.0.0.255 | Конец расчетного периода | Ch. 0 End of billing period | - | - | - | Ch. 0 End of billing period | - | - | - | Yes | Yes | Success
0.0.15.0.1.255 | - | Ch. 0 Disconnect control | - | - | - | Not found | - | - | - | - | - | Fail
0.0.15.0.2.255 | - | Ch. 0 Image activation | - | - | - | Ch. 0 Image activation | - | - | - | Yes | Yes | Success
0.0.15.1.0.255 | - | Ch. 0 End of billing period, implementation specific #2 | - | - | - | Not found | - | - | - | - | - | Fail
0.0.15.2.0.255 | - | Ch. 0 End of billing period, implementation specific #3 | - | - | - | Not found | - | - | - | - | - | Fail
0.0.22.0.0.255 | Настройка IEC HDLC | Ch. 0 IEC HDLC setup | - | - | - | Ch. 0 IEC HDLC setup | - | - | - | Yes | Yes | Success
0.1.22.0.0.255 | Настройка IEC HDLC | Ch. 1 IEC HDLC setup | - | - | - | Ch. 1 IEC HDLC setup | - | - | - | Yes | Yes | Success
0.3.22.0.0.255 | Скорость по интерфейсу связи Р4 | Ch. 3 IEC HDLC setup | - | - | - | Not found | - | - | - | - | - | Fail
0.0.2.0.0.255 | - | Ch. 0 Modem configuration | - | - | - | Not found | - | - | - | - | - | Fail
0.0.2.2.0.255 | - | Ch. 0 Auto answer | - | - | - | Not found | - | - | - | - | - | Fail
0.0.2.1.0.255 | - | Ch. 0 Auto connect | - | - | - | Not found | - | - | - | - | - | Fail
0.0.25.0.0.255 | Настройка TCP/UDP соединения оптопорта Р1 | Ch. 0 TCP-UDP setup | - | - | - | Not found | - | - | - | - | - | Fail
0.0.25.1.0.255 | - | Ch. 0 IPv4 setup | - | - | - | Not found | - | - | - | - | - | Fail
0.0.25.3.0.255 | - | Ch. 0 PPP setup | - | - | - | Not found | - | - | - | - | - | Fail
0.0.25.3.1.255 | - | Invalid | - | - | - | Not found | - | - | - | - | - | Fail
0.0.25.4.0.255 | - | Ch. 0 GPRS modem setup | - | - | - | Not found | - | - | - | - | - | Fail
0.0.25.4.1.255 | - | Invalid | - | - | - | Not found | - | - | - | - | - | Fail
0.0.25.6.0.255 | - | Ch. 0 GSM diagnostic | - | - | - | Not found | - | - | - | - | - | Fail
0.0.43.0.0.255 | - | Ch. 0 Security setup #0 | - | - | - | Ch. 0 Security setup #0 | - | - | - | Yes | Yes | Success
0.0.43.0.2.255 | Настройка | Ch. 0 Security setup #2 | - | - | - | Ch. 0 Security setup #2 | - | - | - | Yes | Yes | Success
0.0.17.0.1.255 | Ток | Ch. 0 Limiter #2 | - | - | - | Ch. 0 Limiter #2 | - | - | - | Yes | Yes | Success
0.0.17.0.2.255 | Напряжение | Ch. 0 Limiter #3 | - | - | - | Ch. 0 Limiter #3 | - | - | - | Yes | Yes | Success
0.0.17.0.3.255 | Магнитное поле | Ch. 0 Limiter #4 | - | - | - | Ch. 0 Limiter #4 | - | - | - | Yes | Yes | Success
0.0.17.0.4.255 | Разбаланс токов | Ch. 0 Limiter #5 | - | - | - | Ch. 0 Limiter #5 | - | - | - | Yes | Yes | Success
0.0.17.0.5.255 | Температура | Ch. 0 Limiter #6 | - | - | - | Ch. 0 Limiter #6 | - | - | - | Yes | Yes | Success
0.0.17.0.6.255 | - | Ch. 0 Limiter #7 | - | - | - | Not found | - | - | - | - | - | Fail
0.1.24.1.0.255 | - | Ch. 1 M-Bus client | - | - | - | Not found | - | - | - | - | - | Fail
0.0.24.6.0.255 | - | Ch. 0 M-Bus master port setup #1 | - | - | - | Not found | - | - | - | - | - | Fail
0.0.44.2.0.255 | - | Invalid | - | - | - | Not found | - | - | - | - | - | Fail
0.1.44.2.0.255 | - | Invalid | - | - | - | Not found | - | - | - | - | - | Fail
0.2.44.2.0.255 | - | Invalid | - | - | - | Not found | - | - | - | - | - | Fail
0.0.40.0.1.255 | Ассоциация «Публичный клиент» | Ch. 0 Association #1 | - | - | - | Ch. 0 Association #1 | - | - | - | Yes | Yes | Success
0.0.40.0.2.255 | Ассоциация 2 «Считыватель показаний» | Ch. 0 Association #2 | - | - | - | Ch. 0 Association #2 | - | - | - | Yes | Yes | Success
0.0.40.0.3.255 | Ассоциация 3 «Конфигуратор» | Ch. 0 Association #3 | - | - | - | Ch. 0 Association #3 | - | - | - | Yes | Yes | Success
0.0.40.0.4.255 | Ассоциация 4 «Инициативный» | Ch. 0 Association #4 | - | - | - | Ch. 0 Association #4 | - | - | - | Yes | Yes | Success
0.0.96.50.100.255 | - | Not found | - | - | - | Ch. 0 Man. spec. abstract object | 9 | Byte sequence | - | - | - | Fail
0.0.96.52.77.255 | - | Not found | - | - | - | Ch. 0 Man. spec. abstract object | 9 | Byte sequence | - | - | - | Fail
0.0.97.98.13.255 | - | Not found | - | - | - | Ch. 0 Alarm filter object #4 | 18 | 16-bit unsigned integer | - | - | - | Fail
0.0.97.98.14.255 | - | Not found | - | - | - | Ch. 0 Alarm filter object #5 | 17 | 8-bit unsigned integer | - | - | - | Fail
0.0.164.0.0.255 | - | Not found | - | - | - | Manufacturer specific | 9 | Byte sequence | - | - | - | Fail
0.0.168.0.0.255 | - | Not found | - | - | - | Manufacturer specific | 2 | Structure from data of different types | - | - | - | Fail
1.0.0.4.2.255 | коэф трансформ по току | Not found | - | - | - | Ch. 0 Transformer ratio - current (numerator) | 18 | 16-bit unsigned integer | - | - | - | Fail
1.0.0.4.3.255 | коэф трансф по напряжению | Not found | - | - | - | Ch. 0 Transformer ratio - voltage (numerator) | 18 | 16-bit unsigned integer | - | - | - | Fail
1.2.0.2.0.255 | - | Not found | - | - | - | Ch. 2 Active firmware identifier | 9 | Byte sequence | - | - | - | Fail
0.0.165.0.0.255 | - | Not found | - | - | - | Manufacturer specific | 18 | 16-bit unsigned integer | 1 | - | - | Fail
0.100.96.6.3.255 | - | Not found | - | - | - | Ch. 100 Utility specific objects | 18 | 16-bit unsigned integer | 0.01 | - | - | Fail
1.0.1.8.5.101 | - | Not found | - | - | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 5 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.1.8.5.255 | Активная энергия, импорт по 5 тарифу | Not found | - | - | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.1.8.6.101 | - | Not found | - | - | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 6 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.1.8.6.255 | Активная энергия, импорт по 6 тарифу | Not found | - | - | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.1.8.7.101 | - | Not found | - | - | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 7 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.1.8.7.255 | Активная энергия, импорт по 7 тарифу | Not found | - | - | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.1.8.8.101 | - | Not found | - | - | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 8 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.1.8.8.255 | Активная энергия, импорт по 8 тарифу | Not found | - | - | - | Ch. 0 Sum Li Active power+ (QI+QIV) Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.2.8.5.101 | - | Not found | - | - | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 5 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.2.8.5.255 | Активная энергия, экспорт по 5 тарифу | Not found | - | - | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.2.8.6.101 | - | Not found | - | - | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 6 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.2.8.6.255 | Активная энергия, экспорт по 6 тарифу | Not found | - | - | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.2.8.7.101 | - | Not found | - | - | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 7 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.2.8.7.255 | Активная энергия, экспорт по 7 тарифу | Not found | - | - | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.2.8.8.101 | - | Not found | - | - | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 8 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.2.8.8.255 | Активная энергия, экспорт по 8 тарифу | Not found | - | - | - | Ch. 0 Sum Li Active power- (QII+QIII) Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.3.8.5.101 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 5 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.3.8.5.255 | Реактивная энергия, импорт по 5 тарифу | Not found | - | - | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.3.8.6.101 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 6 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.3.8.6.255 | Реактивная энергия, импорт по 6 тарифу | Not found | - | - | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.3.8.7.101 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 7 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.3.8.7.255 | Реактивная энергия, импорт по 7 тарифу | Not found | - | - | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.3.8.8.101 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 8 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.3.8.8.255 | Реактивная энергия, импорт по 8 тарифу | Not found | - | - | - | Ch. 0 Sum Li Reactive power+ (QI+QII) Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.4.8.5.101 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 5 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.4.8.5.255 | Реактивная энергия, экспорт по 5 тарифу | Not found | - | - | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.4.8.6.101 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 6 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.4.8.6.255 | Реактивная энергия, экспорт по 6 тарифу | Not found | - | - | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.4.8.7.101 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 7 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.4.8.7.255 | Реактивная энергия, экспорт по 7 тарифу | Not found | - | - | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.4.8.8.101 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 8 (0 is total) 1. last / 1 last billing periods | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.4.8.8.255 | Реактивная энергия, экспорт по 8 тарифу | Not found | - | - | - | Ch. 0 Sum Li Reactive power- (QIII+QIV) Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.0.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.1.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.2.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.3.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.4.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.5.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.6.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.7.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.5.8.8.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QI Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.0.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.1.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.2.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.3.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.4.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.5.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.6.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.7.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.6.8.8.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QII Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.0.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.1.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.2.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.3.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.4.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.5.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.6.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.7.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.7.8.8.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIII Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.0.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.1.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.2.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.3.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.4.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.5.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.6.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.7.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.8.8.8.255 | - | Not found | - | - | - | Ch. 0 Sum Li Reactive power QIV Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.0.255 | Полная энергия | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.1.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.2.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.3.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.4.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.5.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.6.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.7.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.9.8.8.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power+ (QI+QIV) Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.0.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 0 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.1.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 1 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.2.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 2 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.3.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 3 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.4.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 4 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.5.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.6.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.7.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.10.8.8.255 | - | Not found | - | - | - | Ch. 0 Sum Li Apparent power- (QII+QIII) Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.12.46.0.255 | - | Not found | - | - | - | Ch. 0 Voltage: any phase Contracted value Rate 0 (0 is total) | 0 | Missing data | 1 | - | - | Fail
1.0.12.130.0.255 | Установившееся отклонение напряжения, в % со знаком (для однофазных ПУ) | Not found | - | - | - | Man. specific | 5 | 32-bit signed integer | 0.001 | - | - | Fail
1.0.15.6.131.255 | - | Not found | - | - | - | Man. specific | 6 | 32-bit unsigned integer | 0.001 | - | - | Fail
1.0.15.8.5.255 | - | Not found | - | - | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 5 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.15.8.6.255 | - | Not found | - | - | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 6 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.15.8.7.255 | - | Not found | - | - | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 7 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.15.8.8.255 | - | Not found | - | - | - | Ch. 0 Sum Li Active power (abs(QI+QIV)+abs(QII+QIII)) Time integral 1 Rate 8 (0 is total) | 6 | 32-bit unsigned integer | 1 | - | - | Fail
1.0.31.7.0.255 | Ток Ia | Not found | - | - | - | Ch. 0 L1 Current Inst. value | 5 | 32-bit signed integer | 0.001 | - | - | Fail
1.0.32.7.0.255 | Напряжение фазы А | Not found | - | - | - | Ch. 0 L1 Voltage Inst. value | 6 | 32-bit unsigned integer | 0.001 | - | - | Fail
1.0.90.3.0.255 | - | Not found | - | - | - | Ch. 0 SLi current (algebraic sum of the - unsigned - value of the currents in all phases) Min. 1 Rate 0 (0 is total) | 18 | 16-bit unsigned integer | 0.01 | - | - | Fail
1.0.91.35.132.255 | Дифференциальный ток, %. Пороговое значение | Not found | - | - | - | Man. specific | 6 | 32-bit unsigned integer | 0.1 | - | - | Fail
1.0.91.44.132.255 | Дифференциальный ток, %. Пороговое значение по времени | Not found | - | - | - | Man. specific | 17 | 8-bit unsigned integer | 1 | - | - | Fail
1.0.96.57.83.255 | - | Not found | - | - | - | Ch. 0 Manufacturer specific | 5 | 32-bit signed integer | 0.001 | - | - | Fail
1.0.96.57.84.255 | - | Not found | - | - | - | Ch. 0 Manufacturer specific | 5 | 32-bit signed integer | 0.001 | - | - | Fail
0.0.99.98.199.255 | - | Not found | - | - | - | Manufacturer specific | - | - | - | - | - | Fail
0.0.10.0.0.255 | - | Not found | - | - | - | Ch. 0 Global meter reset | - | - | - | - | - | Fail
0.0.10.1.100.255 | - | Not found | - | - | - | Ch. 0 Tariffication script table, implementation specific #2 | - | - | - | - | - | Fail
0.0.10.9.0.255 | - | Not found | - | - | - | Ch. 0 Global meter reset, implementation specific #10 | - | - | - | - | - | Fail
0.0.10.15.0.255 | - | Not found | - | - | - | Ch. 0 Global meter reset, implementation specific #16 | - | - | - | - | - | Fail
0.0.20.0.1.255 | Настройка IEC | Not found | - | - | - | Ch. 0 IEC electrical port setup | - | - | - | - | - | Fail

## 0.0.99.98.0.255
| Профиль: Напряжений | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.0.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
1.0.12.7.0.255 | Напряжение U | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes
1.0.12.7.4.255 | Глубина провала/ перенапряжения | 2 | Yes | Yes | 4 | Yes | Yes | 4 | Yes
0.0.96.8.10.255 | Длительность провала/ перенапряжения | 2 | Yes | Yes | 5 | Yes | Yes | 5 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 6 | Yes | Yes | 6 | Yes

## 0.0.99.98.1.255
| Профиль: Токов | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.1.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.10.255
| Профиль: Состояний дискретных входов и выходов | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Not found | - | - | Not found | - | - | -
0.0.96.3.0.255 | Статус входов/выходов | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Not found | - | - | Not found | - | - | -

## 0.0.99.98.12.255
| Профиль: Выход тангенса за порог на интервале интегрирования | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 8 | Yes | No | 1 | Yes | No | 1 | Yes
1.0.131.27.0.255 | Коэффициент реактивной мощности tg (φ). Среднее значение на интервале интегрирования. | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.13.255
| Профиль: Коррекции времени | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 8 | Yes | No | 1 | Yes | No | 1 | Yes
0.0.1.0.1.255 | Старое время | 8 | Yes | No | 2 | Yes | No | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.14.255
| Профиль: Годовой профиль | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 8 | Yes | No | 1 | Not found | - | - | -
1.0.1.8.1.255 | Активная энергия, импорт по 1 тарифу | 2 | Yes | Yes | 2 | Not found | - | - | -
1.0.1.8.2.255 | Активная энергия, импорт по 2 тарифу | 2 | Yes | Yes | 3 | Not found | - | - | -
1.0.1.8.3.255 | Активная энергия, импорт по 3 тарифу | 2 | Yes | Yes | 4 | Not found | - | - | -
1.0.1.8.4.255 | Активная энергия, импорт по 4 тарифу | 2 | Yes | Yes | 5 | Not found | - | - | -
1.0.1.8.0.255 | Активная энергия, импорт | 2 | Yes | Yes | 6 | Not found | - | - | -
1.0.21.8.0.255 | Активная энергия, фаза А, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.41.8.0.255 | Активная энергия, фаза B, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.61.8.0.255 | Активная энергия, фаза С, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.1.255 | Активная энергия, экспорт по 1 тарифу | 2 | Yes | Yes | 7 | Not found | - | - | -
1.0.2.8.2.255 | Активная энергия, экспорт по 2 тарифу | 2 | Yes | Yes | 8 | Not found | - | - | -
1.0.2.8.3.255 | Активная энергия, экспорт по 3 тарифу | 2 | Yes | Yes | 9 | Not found | - | - | -
1.0.2.8.4.255 | Активная энергия, экспорт по 4 тарифу | 2 | Yes | Yes | 10 | Not found | - | - | -
1.0.2.8.0.255 | Активная энергия, экспорт | 2 | Yes | Yes | 11 | Not found | - | - | -
1.0.22.8.0.255 | Активная энергия, фаза А, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.42.8.0.255 | Активная энергия, фаза B, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.62.8.0.255 | Активная энергия, фаза С, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.1.255 | Реактивная энергия, импорт по 1 тарифу | 2 | Yes | Yes | 12 | Not found | - | - | -
1.0.3.8.2.255 | Реактивная энергия, импорт по 2 тарифу | 2 | Yes | Yes | 13 | Not found | - | - | -
1.0.3.8.3.255 | Реактивная энергия, импорт по 3 тарифу | 2 | Yes | Yes | 14 | Not found | - | - | -
1.0.3.8.4.255 | Реактивная энергия, импорт по 4 тарифу | 2 | Yes | Yes | 15 | Not found | - | - | -
1.0.3.8.0.255 | Реактивная энергия, импорт | 2 | Yes | Yes | 16 | Not found | - | - | -
1.0.23.8.0.255 | Реактивная энергия, фаза А, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.43.8.0.255 | Реактивная энергия, фаза B, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.63.8.0.255 | Реактивная энергия, фаза С, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.1.255 | Реактивная энергия, экспорт по 1 тарифу | 2 | Yes | Yes | 17 | Not found | - | - | -
1.0.4.8.2.255 | Реактивная энергия, экспорт по 2 тарифу | 2 | Yes | Yes | 18 | Not found | - | - | -
1.0.4.8.3.255 | Реактивная энергия, экспорт по 3 тарифу | 2 | Yes | Yes | 19 | Not found | - | - | -
1.0.4.8.4.255 | Реактивная энергия, экспорт по 4 тарифу | 2 | Yes | Yes | 20 | Not found | - | - | -
1.0.4.8.0.255 | Реактивная энергия, экспорт | 2 | Yes | Yes | 21 | Not found | - | - | -
1.0.24.8.0.255 | Реактивная энергия, фаза А, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.44.8.0.255 | Реактивная энергия, фаза B, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.64.8.0.255 | Реактивная энергия, фаза С, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.1.255 | Удельная энергия потерь в ЛЭП, тариф 1 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.2.255 | Удельная энергия потерь в ЛЭП, тариф 2 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.3.255 | Удельная энергия потерь в ЛЭП, тариф 3 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.4.255 | Удельная энергия потерь в ЛЭП, тариф 4 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.0.255 | Удельная энергия потерь в ЛЭП | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.1.255 | Удельная энергия потерь в силовых трансформаторах, тариф 1 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.2.255 | Удельная энергия потерь в силовых трансформаторах, тариф 2 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.3.255 | Удельная энергия потерь в силовых трансформаторах, тариф 3 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.4.255 | Удельная энергия потерь в силовых трансформаторах, тариф 4 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.0.255 | Удельная энергия потерь в силовых трансформаторах | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 22 | Not found | - | - | -

## 0.0.99.98.15.255
| Профиль: Качества сети на расчётный период | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 8 | Yes | No | 1 | Yes | No | 1 | Yes
1.0.147.133.0.255 | Суммарное время отклонения напряжения за расчётный период | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
1.0.148.36.0.255 | Количество перенапряжений за расчётный период | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 4 | Yes | Yes | 4 | Yes

## 0.0.99.98.16.255
| Профиль: Контроль мощности | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 8 | Yes | No | 1 | Yes | No | 1 | Yes
0.0.96.5.2.255 | Слово состояний контроля мощности | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.17.255
| Профиль: Батарея | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 8 | Not found | - | - | Not found | - | - | -
0.0.96.6.1.255 | Состояние батареи | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Not found | - | - | Not found | - | - | -

## 0.0.99.98.18.255
| Профиль: Контроль блокиратора реле нагрузки | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 8 | Yes | No | 1 | Yes | No | 1 | Yes
0.0.96.4.3.255 | Блокировка реле нагрузки | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.19.255
| Профиль: Контроль температуры* | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 8 | Not found | - | - | Not found | - | - | -
0.0.96.5.128.255 | Слово состояний контроля температуры | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Not found | - | - | Not found | - | - | -

## 0.0.99.98.2.255
| Профиль: Включений/ выключений | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.2.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.28.255
| Профиль: Нештатная ситуация сети* | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Not found | - | - | Not found | - | - | -
0.0.95.5.130.255 | Слово состояний нештатной ситуации сети | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Not found | - | - | Not found | - | - | -

## 0.0.99.98.3.255
| Профиль: Коррекций данных | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.3.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.12.4.255 | Номер канала (интерфейс) | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 4 | Yes | Yes | 4 | Yes

## 0.0.99.98.4.255
| Профиль: Внешних воздействий | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.4.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.5.255
| Профиль: Коммуникационные события | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.5.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.12.4.255 | Номер канала (интерфейс) | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes
0.0.96.12.6.255 | Адрес (клиента) | 2 | Yes | Yes | 4 | Yes | Yes | 4 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 5 | Yes | Yes | 5 | Yes

## 0.0.99.98.6.255
| Профиль: Контроль доступа | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.6.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.12.4.255 | Номер канала (интерфейс) | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes
0.0.96.12.6.255 | Адрес (клиента) | 2 | Yes | Yes | 4 | Yes | Yes | 4 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 5 | Yes | Yes | 5 | Yes

## 0.0.99.98.7.255
| Профиль: Самодиагностики | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.7.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.8.255
| Профиль: Превышение тангенса | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.11.8.255 | Код события | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 0.0.99.98.9.255
| Профиль: Параметры качества сети | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
0.0.96.5.4.255 | Статус качества сети | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
0.0.96.8.0.255 | Время работы счетчика | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes

## 1.0.94.7.0.255
| Профиль: Текущие значения | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
1.0.31.7.0.255 | Ток Ia | 2 | Not found | - | - | Not found | - | - | -
1.0.51.7.0.255 | Ток Ib | 2 | Not found | - | - | Not found | - | - | -
1.0.71.7.0.255 | Ток Ic | 2 | Not found | - | - | Not found | - | - | -
1.0.91.7.0.255 | Ток I0 | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes
1.0.91.132.0.255 | - | 2 | Not found | - | - | Not found | - | - | -
1.0.32.7.0.255 | Напряжение фазы А | 2 | Not found | - | - | Not found | - | - | -
1.0.52.7.0.255 | Напряжение вазы В | 2 | Not found | - | - | Not found | - | - | -
1.0.72.7.0.255 | Напряжение фазы С | 2 | Not found | - | - | Not found | - | - | -
1.0.33.7.0.255 | Коэф. мощности фазы А | 2 | Not found | - | - | Not found | - | - | -
1.0.53.7.0.255 | Коэф. мощности фазы B | 2 | Not found | - | - | Not found | - | - | -
1.0.73.7.0.255 | Коэф. мощности фазы C | 2 | Not found | - | - | Not found | - | - | -
1.0.13.7.0.255 | Суммарный коэф. мощности | 2 | Yes | Yes | 5 | Yes | Yes | 5 | Yes
1.0.14.7.0.255 | Частота сети F | 2 | Yes | Yes | 6 | Yes | Yes | 6 | Yes
1.0.9.7.0.255 | Суммарная полная мощность | 2 | Yes | Yes | 7 | Yes | Yes | 7 | Yes
1.0.29.7.0.255 | Полная мощность фазы А | 2 | Not found | - | - | Not found | - | - | -
1.0.49.7.0.255 | Полная мощность фазы B | 2 | Not found | - | - | Not found | - | - | -
1.0.69.7.0.255 | Полная мощность фазы C | 2 | Not found | - | - | Not found | - | - | -
1.0.1.7.0.255 | Суммарная активная мощность | 2 | Yes | Yes | 8 | Yes | Yes | 8 | Yes
1.0.21.7.0.255 | Активная мощность фазы А | 2 | Not found | - | - | Not found | - | - | -
1.0.41.7.0.255 | Активная мощность фазы B | 2 | Not found | - | - | Not found | - | - | -
1.0.61.7.0.255 | Активная мощность фазы C | 2 | Not found | - | - | Not found | - | - | -
1.0.3.7.0.255 | Суммарная реактивная мощность | 2 | Yes | Yes | 9 | Yes | Yes | 9 | Yes
1.0.23.7.0.255 | Реактивная мощность фазы А | 2 | Not found | - | - | Not found | - | - | -
1.0.43.7.0.255 | Реактивная мощность фазы B | 2 | Not found | - | - | Not found | - | - | -
1.0.63.7.0.255 | Реактивная мощность фазы C | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.0.255 | Активная энергия, импорт | 2 | Yes | Yes | 10 | Yes | Yes | 10 | Yes
1.0.2.8.0.255 | Активная энергия, экспорт | 2 | Yes | Yes | 11 | Yes | Yes | 11 | Yes
1.0.3.8.0.255 | Реактивная энергия, импорт | 2 | Yes | Yes | 12 | Yes | Yes | 12 | Yes
1.0.4.8.0.255 | Реактивная энергия, экспорт | 2 | Yes | Yes | 13 | Yes | Yes | 13 | Yes
1.0.88.8.0.255 | Удельная энергия потерь в ЛЭП | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.0.255 | Удельная энергия потерь в силовых трансформаторах | 2 | Not found | - | - | Not found | - | - | -
1.0.124.7.0.255 | Линейное напряжение АВ | 2 | Not found | - | - | Not found | - | - | -
1.0.125.7.0.255 | Линейное напряжение ВС | 2 | Not found | - | - | Not found | - | - | -
1.0.126.7.0.255 | Линейное напряжение СА | 2 | Not found | - | - | Not found | - | - | -
1.0.15.16.0.255 | Суточное значение максимальной активной мощности на интервале интегрирования 2 | 2 | Not found | - | - | Not found | - | - | -
1.0.15.16.1.255 | Суточное значение максимальной активной мощности на интервале интегрирования 2 в период пиковых нагрузок | 2 | Not found | - | - | Not found | - | - | -
1.0.21.8.0.255 | Активная энергия, фаза А, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.41.8.0.255 | Активная энергия, фаза B, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.61.8.0.255 | Активная энергия, фаза С, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.22.8.0.255 | Активная энергия, фаза А, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.42.8.0.255 | Активная энергия, фаза B, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.62.8.0.255 | Активная энергия, фаза С, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.23.8.0.255 | Реактивная энергия, фаза А, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.43.8.0.255 | Реактивная энергия, фаза B, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.63.8.0.255 | Реактивная энергия, фаза С, импорт | 2 | Not found | - | - | Not found | - | - | -
1.0.24.8.0.255 | Реактивная энергия, фаза А, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.44.8.0.255 | Реактивная энергия, фаза B, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.64.8.0.255 | Реактивная энергия, фаза С, экспорт | 2 | Not found | - | - | Not found | - | - | -
1.0.128.7.0.255 | Коэффициент реактивной мощности фазы А | 2 | Not found | - | - | Not found | - | - | -
1.0.129.7.0.255 | Коэффициент реактивной мощности фазы B | 2 | Not found | - | - | Not found | - | - | -
1.0.130.7.0.255 | Коэффициент реактивной мощности фазы C | 2 | Not found | - | - | Not found | - | - | -
1.0.131.7.0.255 | Суммарный коэффициент реактивной мощности | 2 | Yes | Yes | 14 | Yes | Yes | 15 | No
1.0.11.7.0.255 | Ток I | 2 | i100-XML.XML | - | - | Нартис-100 LY.XML | - | - | -
1.0.12.7.0.255 | Напряжение U | 2 | i100-XML.XML | - | - | Нартис-100 LY.XML | - | - | -
1.0.91.7.131.255 | Диф. Ток | 2 | i100-XML.XML | - | - | Нартис-100 LY.XML | - | - | -

## 1.0.94.7.6.255
| Профиль: Телесигнализации* | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Not found | - | - | Not found | - | - | -
0.0.96.11.0.255 | Код события | 2 | Not found | - | - | Not found | - | - | -
0.0.96.11.2.255 | Код события | 2 | Not found | - | - | Not found | - | - | -
0.0.96.11.4.255 | Код события | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Not found | - | - | Not found | - | - | -

## 1.0.98.1.0.255
| Профиль: Месячный | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
1.0.1.8.0.255 | Активная энергия, импорт | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
1.0.1.8.1.255 | Активная энергия, импорт по 1 тарифу | 2 | Yes | Yes | 6 | Yes | Yes | 3 | No
1.0.1.8.2.255 | Активная энергия, импорт по 2 тарифу | 2 | Yes | Yes | 7 | Yes | Yes | 4 | No
1.0.1.8.3.255 | Активная энергия, импорт по 3 тарифу | 2 | Yes | Yes | 8 | Yes | Yes | 5 | No
1.0.1.8.4.255 | Активная энергия, импорт по 4 тарифу | 2 | Yes | Yes | 9 | Yes | Yes | 6 | No
1.0.1.8.5.255 | Активная энергия, импорт по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.6.255 | Активная энергия, импорт по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.7.255 | Активная энергия, импорт по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.8.255 | Активная энергия, импорт по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.0.255 | Реактивная энергия, импорт | 2 | Yes | Yes | 4 | Yes | Yes | 12 | No
1.0.4.8.0.255 | Реактивная энергия, экспорт | 2 | Yes | Yes | 5 | Yes | Yes | 17 | No
1.0.9.8.0.255 | Полная энергия | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.0.255 | Активная энергия, экспорт | 2 | Yes | Yes | 3 | Yes | Yes | 7 | No
1.0.1.6.0.255 | Максимальная мощность на расчётном периоде и дата время начала интервала максимальной мощности | 2 | Yes | No | 23 | Not found | - | - | -
1.0.1.6.0.255 | Максимальная мощность на расчётном периоде и дата время начала интервала максимальной мощности | 5 | Not found | - | - | Not found | - | - | -
1.0.88.8.0.255 | Удельная энергия потерь в ЛЭП | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.0.255 | Удельная энергия потерь в силовых трансформаторах | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.1.255 | Активная энергия, экспорт по 1 тарифу | 2 | Yes | Yes | 10 | Yes | Yes | 8 | No
1.0.2.8.2.255 | Активная энергия, экспорт по 2 тарифу | 2 | Yes | Yes | 11 | Yes | Yes | 9 | No
1.0.2.8.3.255 | Активная энергия, экспорт по 3 тарифу | 2 | Yes | Yes | 12 | Yes | Yes | 10 | No
1.0.2.8.4.255 | Активная энергия, экспорт по 4 тарифу | 2 | Yes | Yes | 13 | Yes | Yes | 11 | No
1.0.2.8.5.255 | Активная энергия, экспорт по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.6.255 | Активная энергия, экспорт по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.7.255 | Активная энергия, экспорт по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.8.255 | Активная энергия, экспорт по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.1.255 | Реактивная энергия, импорт по 1 тарифу | 2 | Yes | Yes | 14 | Yes | Yes | 13 | No
1.0.3.8.2.255 | Реактивная энергия, импорт по 2 тарифу | 2 | Yes | Yes | 15 | Yes | Yes | 14 | No
1.0.3.8.3.255 | Реактивная энергия, импорт по 3 тарифу | 2 | Yes | Yes | 16 | Yes | Yes | 15 | No
1.0.3.8.4.255 | Реактивная энергия, импорт по 4 тарифу | 2 | Yes | Yes | 17 | Yes | Yes | 16 | No
1.0.3.8.5.255 | Реактивная энергия, импорт по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.6.255 | Реактивная энергия, импорт по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.7.255 | Реактивная энергия, импорт по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.8.255 | Реактивная энергия, импорт по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.1.255 | Реактивная энергия, экспорт по 1 тарифу | 2 | Yes | Yes | 18 | Yes | Yes | 18 | Yes
1.0.4.8.2.255 | Реактивная энергия, экспорт по 2 тарифу | 2 | Yes | Yes | 19 | Yes | Yes | 19 | Yes
1.0.4.8.3.255 | Реактивная энергия, экспорт по 3 тарифу | 2 | Yes | Yes | 20 | Yes | Yes | 20 | Yes
1.0.4.8.4.255 | Реактивная энергия, экспорт по 4 тарифу | 2 | Yes | Yes | 21 | Yes | Yes | 21 | Yes
1.0.4.8.5.255 | Реактивная энергия, экспорт по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.6.255 | Реактивная энергия, экспорт по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.7.255 | Реактивная энергия, экспорт по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.8.255 | Реактивная энергия, экспорт по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.1.255 | Удельная энергия потерь в ЛЭП, тариф 1 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.2.255 | Удельная энергия потерь в ЛЭП, тариф 2 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.3.255 | Удельная энергия потерь в ЛЭП, тариф 3 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.4.255 | Удельная энергия потерь в ЛЭП, тариф 4 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.5.255 | Удельная энергия потерь в ЛЭП по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.6.255 | Удельная энергия потерь в ЛЭП по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.7.255 | Удельная энергия потерь в ЛЭП по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.8.255 | Удельная энергия потерь в ЛЭП по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.1.255 | Удельная энергия потерь в силовых трансформаторах, тариф 1 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.2.255 | Удельная энергия потерь в силовых трансформаторах, тариф 2 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.3.255 | Удельная энергия потерь в силовых трансформаторах, тариф 3 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.4.255 | Удельная энергия потерь в силовых трансформаторах, тариф 4 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.5.255 | Удельная энергия потерь в силовых трансформаторах по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.6.255 | Удельная энергия потерь в силовых трансформаторах по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.7.255 | Удельная энергия потерь в силовых трансформаторах по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.8.255 | Удельная энергия потерь в силовых трансформаторах по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.0.8.5.255 | Интервал интегрирования 2 параметров сети | 2 | Not found | - | - | Not found | - | - | -
1.0.131.6.128.255 | Коэффициент реактивной мощности tg (φ). Максимальное значение на интервале интегрирования 2 за расчетный период | 2 | Yes | Yes | 24 | Not found | - | - | -
1.0.9.3.128.255 | Минимальное значение полной мощности на интервале интегрирования 2 за расчетный период | 2 | Yes | Yes | 25 | Not found | - | - | -
1.0.9.6.128.255 | Максимальное значение полной мощности на интервале интегрирования 2 за расчетный период | 2 | Yes | Yes | 26 | Not found | - | - | -
1.0.15.3.128.255 | Минимальное значение активной мощности на интервале интегрирования 2 за расчетный период | 2 | Yes | Yes | 27 | Not found | - | - | -
1.0.15.6.128.255 | Максимальное значение активной мощности на интервале интегрирования 2 за расчетный период | 2 | Yes | Yes | 28 | Not found | - | - | -
1.0.137.3.128.255 | Минимальное значение реактивной мощности на интервале интегрирования 2 за расчетный период | 2 | Yes | Yes | 29 | Not found | - | - | -
1.0.137.6.128.255 | Максимальное значение реактивной мощности на интервале интегрирования 2 за расчетный период | 2 | Yes | Yes | 30 | Not found | - | - | -
1.0.15.6.129.255 | Усредненное за месяц суточное значение максимальной активной мощности на интервале интегрирования 2 | 2 | Yes | Yes | 31 | Not found | - | - | -
1.0.15.6.130.255 | Усредненное за месяц суточное значение максимальной активной мощности на интервале интегрирования 2 в период пиковых нагрузок | 2 | Yes | Yes | 32 | Not found | - | - | -

## 1.0.98.2.0.255
| Профиль: Суточный | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
1.0.1.8.1.255 | Активная энергия, импорт по 1 тарифу | 2 | Yes | Yes | 6 | Yes | Yes | 3 | No
1.0.1.8.2.255 | Активная энергия, импорт по 2 тарифу | 2 | Yes | Yes | 7 | Yes | Yes | 4 | No
1.0.1.8.3.255 | Активная энергия, импорт по 3 тарифу | 2 | Yes | Yes | 8 | Yes | Yes | 5 | No
1.0.1.8.4.255 | Активная энергия, импорт по 4 тарифу | 2 | Yes | Yes | 9 | Yes | Yes | 6 | No
1.0.1.8.5.255 | Активная энергия, импорт по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.6.255 | Активная энергия, импорт по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.7.255 | Активная энергия, импорт по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.8.255 | Активная энергия, импорт по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.0.255 | Активная энергия, импорт | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
1.0.2.8.0.255 | Активная энергия, экспорт | 2 | Yes | Yes | 3 | Yes | Yes | 7 | No
1.0.3.8.0.255 | Реактивная энергия, импорт | 2 | Yes | Yes | 4 | Yes | Yes | 12 | No
1.0.4.8.0.255 | Реактивная энергия, экспорт | 2 | Yes | Yes | 5 | Yes | Yes | 17 | No
1.0.88.8.0.255 | Удельная энергия потерь в ЛЭП | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.0.255 | Удельная энергия потерь в силовых трансформаторах | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.1.255 | Время отклонения частоты от нормируемых параметров | 2 | Not found | - | - | Not found | - | - | -
0.0.96.5.1.255 | Статус некачественной энергии | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.1.255 | Активная энергия, экспорт по 1 тарифу | 2 | Yes | Yes | 10 | Yes | Yes | 8 | No
1.0.2.8.2.255 | Активная энергия, экспорт по 2 тарифу | 2 | Yes | Yes | 11 | Yes | Yes | 9 | No
1.0.2.8.3.255 | Активная энергия, экспорт по 3 тарифу | 2 | Yes | Yes | 12 | Yes | Yes | 10 | No
1.0.2.8.4.255 | Активная энергия, экспорт по 4 тарифу | 2 | Yes | Yes | 13 | Yes | Yes | 11 | No
1.0.2.8.5.255 | Активная энергия, экспорт по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.6.255 | Активная энергия, экспорт по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.7.255 | Активная энергия, экспорт по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.8.255 | Активная энергия, экспорт по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.1.255 | Реактивная энергия, импорт по 1 тарифу | 2 | Yes | Yes | 14 | Yes | Yes | 13 | No
1.0.3.8.2.255 | Реактивная энергия, импорт по 2 тарифу | 2 | Yes | Yes | 15 | Yes | Yes | 14 | No
1.0.3.8.3.255 | Реактивная энергия, импорт по 3 тарифу | 2 | Yes | Yes | 16 | Yes | Yes | 15 | No
1.0.3.8.4.255 | Реактивная энергия, импорт по 4 тарифу | 2 | Yes | Yes | 17 | Yes | Yes | 16 | No
1.0.3.8.5.255 | Реактивная энергия, импорт по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.6.255 | Реактивная энергия, импорт по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.7.255 | Реактивная энергия, импорт по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.8.255 | Реактивная энергия, импорт по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.1.255 | Реактивная энергия, экспорт по 1 тарифу | 2 | Yes | Yes | 18 | Yes | Yes | 18 | Yes
1.0.4.8.2.255 | Реактивная энергия, экспорт по 2 тарифу | 2 | Yes | Yes | 19 | Yes | Yes | 19 | Yes
1.0.4.8.3.255 | Реактивная энергия, экспорт по 3 тарифу | 2 | Yes | Yes | 20 | Yes | Yes | 20 | Yes
1.0.4.8.4.255 | Реактивная энергия, экспорт по 4 тарифу | 2 | Yes | Yes | 21 | Yes | Yes | 21 | Yes
1.0.4.8.5.255 | Реактивная энергия, экспорт по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.6.255 | Реактивная энергия, экспорт по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.7.255 | Реактивная энергия, экспорт по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.8.255 | Реактивная энергия, экспорт по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.1.255 | Удельная энергия потерь в ЛЭП, тариф 1 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.2.255 | Удельная энергия потерь в ЛЭП, тариф 2 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.3.255 | Удельная энергия потерь в ЛЭП, тариф 3 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.4.255 | Удельная энергия потерь в ЛЭП, тариф 4 | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.5.255 | Удельная энергия потерь в ЛЭП по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.6.255 | Удельная энергия потерь в ЛЭП по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.7.255 | Удельная энергия потерь в ЛЭП по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.88.8.8.255 | Удельная энергия потерь в ЛЭП по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.1.255 | Удельная энергия потерь в силовых трансформаторах, тариф 1 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.2.255 | Удельная энергия потерь в силовых трансформаторах, тариф 2 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.3.255 | Удельная энергия потерь в силовых трансформаторах, тариф 3 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.4.255 | Удельная энергия потерь в силовых трансформаторах, тариф 4 | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.5.255 | Удельная энергия потерь в силовых трансформаторах по 5 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.6.255 | Удельная энергия потерь в силовых трансформаторах по 6 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.7.255 | Удельная энергия потерь в силовых трансформаторах по 7 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.89.8.8.255 | Удельная энергия потерь в силовых трансформаторах по 8 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.15.16.0.255 | Суточное значение максимальной активной мощности на интервале интегрирования 2 | 2 | Not found | - | - | Not found | - | - | -
1.0.15.16.1.255 | Суточное значение максимальной активной мощности на интервале интегрирования 2 в период пиковых нагрузок | 2 | Not found | - | - | Not found | - | - | -
1.0.0.8.5.255 | Интервал интегрирования 2 параметров сети | 2 | Not found | - | - | Not found | - | - | -

## 1.0.99.1.0.255
| Профиль: Нагрузки | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Yes | Yes | 1 | Yes
1.0.1.29.0.255 | Активная энергия, импорт за период записи | 2 | Yes | Yes | 2 | Yes | Yes | 2 | Yes
1.0.2.29.0.255 | Активная энергия, экспорт за период записи | 2 | Yes | Yes | 3 | Yes | Yes | 3 | Yes
1.0.3.29.0.255 | Реактивная энергия, импорт, за период записи | 2 | Yes | Yes | 4 | Yes | Yes | 4 | Yes
1.0.4.29.0.255 | Реактивная энергия, экспорт, за период записи | 2 | Yes | Yes | 5 | Yes | Yes | 5 | Yes
1.0.9.29.0.255 | Полная энергия, импорт, за период записи | 2 | Not found | - | - | Not found | - | - | -
1.0.10.29.0.255 | Полная энергия, экспорт, за период записи | 2 | Not found | - | - | Not found | - | - | -
1.0.32.7.0.255 | Напряжение фазы А | 2 | Not found | - | - | Not found | - | - | -
1.0.52.7.0.255 | Напряжение вазы В | 2 | Not found | - | - | Not found | - | - | -
1.0.72.7.0.255 | Напряжение фазы С | 2 | Not found | - | - | Not found | - | - | -
1.0.124.7.0.255 | Линейное напряжение АВ | 2 | Not found | - | - | Not found | - | - | -
1.0.125.7.0.255 | Линейное напряжение ВС | 2 | Not found | - | - | Not found | - | - | -
1.0.126.7.0.255 | Линейное напряжение СА | 2 | Not found | - | - | Not found | - | - | -
0.0.96.9.0.255 | Температура внутри корпуса ПУ | 2 | Not found | - | - | Not found | - | - | -
0.0.96.5.129.255 | Статус записи | 2 | Not found | - | - | Not found | - | - | -
0.0.96.8.0.255 | Время работы счетчика | 2 | Not found | - | - | Not found | - | - | -

## 1.0.99.2.0.255
| Профиль: Часовой профиль | Attribute | i100-XML.XML |  |  | Нартис-100 LY.XML
|  |  | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | OBIS(is found/not found) | Attribute coincidence(yes/no) | Index | Index coincidence(yes/no)
OBIS
0.0.1.0.0.255 | Дата и время захвата | 2 | Yes | Yes | 1 | Not found | - | - | -
1.0.1.8.1.255 | Активная энергия, импорт по 1 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.2.255 | Активная энергия, импорт по 2 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.3.255 | Активная энергия, импорт по 3 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.4.255 | Активная энергия, импорт по 4 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.1.8.0.255 | Активная энергия, импорт | 2 | Yes | Yes | 2 | Not found | - | - | -
1.0.2.8.0.255 | Активная энергия, экспорт | 2 | Yes | Yes | 3 | Not found | - | - | -
1.0.3.8.0.255 | Реактивная энергия, импорт | 2 | Yes | Yes | 4 | Not found | - | - | -
1.0.4.8.0.255 | Реактивная энергия, экспорт | 2 | Yes | Yes | 5 | Not found | - | - | -
1.0.2.8.1.255 | Активная энергия, экспорт по 1 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.2.255 | Активная энергия, экспорт по 2 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.3.255 | Активная энергия, экспорт по 3 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.2.8.4.255 | Активная энергия, экспорт по 4 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.1.255 | Реактивная энергия, импорт по 1 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.2.255 | Реактивная энергия, импорт по 2 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.3.255 | Реактивная энергия, импорт по 3 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.3.8.4.255 | Реактивная энергия, импорт по 4 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.1.255 | Реактивная энергия, экспорт по 1 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.2.255 | Реактивная энергия, экспорт по 2 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.3.255 | Реактивная энергия, экспорт по 3 тарифу | 2 | Not found | - | - | Not found | - | - | -
1.0.4.8.4.255 | Реактивная энергия, экспорт по 4 тарифу | 2 | Not found | - | - | Not found | - | - | -

## Files versions
File name | Modification time
i100-XML.XML | Fri Sep 15 14:17:44 2023
Нартис-100 LY.XML | Wed Sep 20 15:13:58 2023
OBISNameRusEng.xlsx | Mon Sep 25 16:15:12 2023